X1.GW531B.TY.F01M.Manufacturer Instruction Manual.
[image: image20.png]


 X1.GW531B.TY.F01M.Manufacturer Instruction Manual.                                                      1

PUNP ELECTRONIC                                            [image: image1.png]



GW531B Cooler Controller

Manufacturer Instruction Manual
	Please read the in manual carefully before installing the controller!

PUNP ELECTRONICS Co., Ltd.   NOV 29, 2013
Software  Version :  X1.GW531B.TY.F01M   V100A5
All rights reserved. Any reproduction of the manual will be prosecuted.


Table of contents
11 Instructions


12 Specifications


13 Panel Diagram


14 First Power-on


25 Common Screens


25.1 Main Screen


25.2 Alarm Screen


26 Common Operation


26.1 Quick Modification of Setting Temperature


26.2 Query/Reset Fault


27 Function Menu


28 Parameter Operation


39 User Parameters Table


310 Manufacturer Menu


310.1 Procedures of Entering Manufacturer Menu


310.2 Details of Manufacturer Menu


410.3 Manufacturer Debugging


410.4 Configuration Wizard


511 Fault List


712 Control


713 Manufacturer Parameters Table


1014 Electrical Connection Diagram


1015 Installation Dimensions




1 Instructions
Dear Customer:

Thank you for choosing PUNP products!

For your convenience, please read the instructions carefully and follow the steps of the Manual.

2 Specifications
	No.
	Specification Parameter
	Description 
	
	No.
	Specification Parameter
	Description 

	1
	Power Supply
	220V/AC±10%  50/60HZ
	
	6
	Switch Output
	4 relays

	2
	Temperature Range
	-40~100℃
	
	7
	Switch Input
	8 passive signal inputs

	3
	Measurement Accuracy
	0.1℃@25℃
	
	8
	Analog Input
	1 NTC temperature sensor

	4
	Working Environment
	-20℃~70℃,≤85%RH non-condensation
	
	9
	Current Input
	3 ways of current (0.3~35A)

	5
	Storage Environment
	-30℃~85℃,≤85%RH non-condensation
	
	
	
	


3 Panel Diagram

[image: image2.emf] 

Alarm

泵

Pump

压缩机

Compressor

向下

Down

向上

Up

Remote

远程

Industrial   Chiller

故障

6531-1-001-100

功能

Function

确定

OK

Light

：

Remote 

ON/OFF is allowed

Black out

：

Remote 

ON/OFF is forbided

Black out

：

Comp run is not allow

Twinkle

：

Com run is allow

Light

：

Comp is running

Twinkle

：

Unit alarm

Black out

：

No alarm

To switch the comp 

run is Allow or not

Black out

：

Pump stoped

Twinkle

：

Pump stoping

Light

：

Pump running

Units ON/OFF

Menu, Cancel, Back, Shift

Add value, Change page, 

Choose parameter

Decrease value, Change 

page, Choose parameter

OK, Query, Reset, Enter


4 First Power-on
The controller needs to be configured when powered on for the first time. Please refer to 10.4 Configuration Wizard for specific operation.

5 Common Screens
Commonly used screens include the main screen and the alarm screen.

	5.1 Main Screen
	5.2 Alarm Screen

	The system will enter the main screen after countdown, which displays as follows:


[image: image3.emf]℃

12.0

℃

Set

Menu

PV

Fn

Liquid temperature

Set temperature


	In case of unit failure, the alarm screen is as follows:

[image: image4.emf]Menu

PV

Fn

Display flickeringly

Alarm

!

℃

20.5

Query

Liquid temperature

OK

Silence&Query




6 Common Operation
	6.1 Quick Modification of Setting Temperature
	6.2 Query/Reset Fault

	If the user parameter [Locked T.set] is set to "No", the setting temperature can be modified directly in the main screen, with operation details as follows:


[image: image5.emf]℃

12.0

℃

Set

Menu

PV

Fn

℃

11.9

℃

Menu

PV

Fn

℃

11.9

℃

Menu

PV

Fn

Set Set

Main screen Change set temperature Main screen


Note: the setting temperature can also be modified in the user parameters.
	In case of fault, the alarm screen will automatically pop up. The operation details of query and reset faults are as follows: 


[image: image6.emf]Menu

PV

Fn

Alarm

!

℃

20.5

Query

℃

12.0

℃

Set

Menu

PV

Fn

Back

Fn

Probe break

Reset

OK

Alarm screen Current  Fault Main screen

OK





7 Function Menu
Press the button 
[image: image7.emf] on the main screen to enter the Function Menu, which includes five items as the table below:

	No.
	Menu Item
	Funtion 
	Remark

	1
	User Settings
	To display user parameters
	For number of user parameters and their implications, please refer to: 9 User Parameters Table.

	2
	Unit Status
	To display the current operating status of the unit 
	Current value is not displayed when current module is not used.

	3
	History List
	Allowing the query of the last 10 faults 
	Press 
[image: image8.emf]for 2s to clear the fault history. 

	4
	Comp Run Time 
	To display the cumulative operation time of the compressor 
	

	5
	Version 
	To check the current software version 
	


8 Parameter Operation

For the modification operation of parameter value, the user’s modification of setting temperature will be described as an example.

[image: image9.emf]Back

Fn

1:User setting

Enter

Function Menu

3:History List

2:Unit status

Back

Fn

Lock T.set:

Set

No

Back

Fn

T.setpoint:

Set

12.0    

℃

Enter user setting

Choice parameter

Cancel

Fn

T.setpoint:

Ok

12.0   

℃

Cancel

Fn

T.setpoint:

Ok

11.9   

℃

Back

Fn

Set

11.9    

℃

Enter parameter

value set

Set parameter value

Save parameter value

T.setpoint:

OK OK OK OK

OK OK


9 User Parameters Table

The implication of each parameter in the user parameters is listed in the following table:

	No.
	Parameter Name
	Factory Default
	Setting Range
	Remark 

	1
	Locked T.set 
	No 
	Yes ~ No
	Yes: the set temperature can not be modified on the main screen when locked.

No: the set temperature can be modified on the main screen.

	2
	T.setpoint
	12.0℃
	-38.0~99.9℃
	Setting range is limited by the manufacturer parameters [T.setpoint min], [T.setpoint max].

	3
	Contrast
	32
	20~44
	Adjust the LCD contrast

	4
	On/Off type
	Local
	Local / Local + Remote / Remote
	Local: the unit can only start and stop locally.

Local + Remote: the start and stop of the unit can be controlled both locally and remotely.

Remote: the unit can only start and stop remotely.

	5
	Backlight On
	0
	0~255 minute(s)
	0: backlight is not turned off. 

	6
	Language
	Chinese 
	Chinese~English
	Select the display language.


10 Manufacturer Menu

Press 
[image: image10.emf]+
[image: image11.emf] in the main screen to enter the Enter Password screen and enter the correct manufacturer password (default 4561, which is recommended to change). Then enter the Manufacturer Function Menu, which includes five items.

10.1 Procedures of Entering Manufacturer Menu 


[image: image12.emf]Shift

Fn

Enter password

Ok

0***

Enter password screen

Chang password Shift to next

Back

Fn

Enter

If password is right,

enter the factory menu 

℃

12.0

℃

Set

Menu

PV

Fn

+

4*** *0**

***1

1:Manuf.Setting

2:Manuf. Debug

3:Config Guide

Main Screen

enter password 

has accomplished

Enter password Enter password

Enter password

Shift

Fn

Ok

Shift

Fn

Ok

Shift

Fn

Ok

OK OK OK

OK

OK


10.2 Details of Manufacturer Menu

The details and function of manufacturer menu are shown in the following table: 

	No.
	Parameter Item
	Function
	Remark s

	1
	Manuf.setting
	To set the parameters commonly 
used by the manufacturer
	Refer to 13 Manufacture Parameters for specific parameters.

	2
	Manuf.Debug
	To debug the abnormal operation of each electrical part of the unit
	Not available during the unit operation.

	3
	Config Wizard
	Commonly used parameters of config the unit
	Not available during the unit operation.

The screen will pop up when 
powered on for the first time.

	4
	Initialize
	For initialize all parameters of the machine.
	Refer to 10.5 Manufacture
Parameters for the initial values of the parameters.

	5
	Password Set
	To set the password to enter manufacturer menu.
	The default value is 4561, which is recommended to change.


Note: Press 
[image: image13.emf]+
[image: image14.emf] in the manufacturer menu for 2 seconds can reset the accumulative operation time of the compressor.
10.3 Manufacturer Debugging

Manufacturer debugging is mainly used to test whether the operation of each electrical part of the unit is normal, which is not available when the unit is under operation. 
Method: to determine whether the unit is normal by testing three-phase power input, seven alarm inputs (10 alarm inputs for two compressors) and 5 relay outputs. For alarm input, it only displays the test result. If the result is normal the wiring is good and parameter settings are correct; if it alarms, with flashing display of alarm characters, then make sure whether the external wiring is good and the parameter settings are consistent.


[image: image15.emf]Cancel

Fn

Enter

Factory debug screen

Back

Fn

Low1 press:

Alarm

Back

Fn

ON

The result of I/O input

choice

Relay output

Manuf. Debug

or

Relay stop output

Back

Fn

High1 Press

：

Normal

Enter factory debug

Back

Fn

OFF

Back

Fn

ON

Press

OK

OK

OK

OK

Pump:

Comp:

Cool:

Alarm:

Pump:

Comp:

Cool:

Alarm:

Pump:

Comp:

Cool:

Alarm:


10.4 Configuration Wizard
Configure the common parameters of the machine. For the number of parameters of configuration wizard and the significance, please refer to 13 Manufacturer Parameters Table. Access is not available during the unit operation. 
Refer to the Parameter Operation for specific configuration method. The Configuration Wizard screen will pop up when powered on for the first time. And if you click “Cancel” operation without configuring at this point, the Configuration Wizard screen will still pop up when powered on next time. Once you have entered the Configuration Wizard, the Configuration Wizard screen will not pop up when powered on and you can only enter the Configuration Wizard through the Manufacturer Menu.


[image: image16.emf]Cancel Enter

Config Guide

Config Guide

Enter

：

the screen will

not pop  up  when 

powered on next time

Cancel

：

the screen will 

still pop up when 

powered on next time

℃

12.0

℃

Menu

PV

Fn

Set

Back

One-Key start:

Set

Forbid

the number of parameters of 

configuration wizard  and the 

significance, please refer to 13 

Manufacturer Parameters Table Fn

Fn

OK

OK


11 Fault List
	Fault
	Description
	Test Conditions
	Troubleshooting 
	Solution 

	Comp.P high
	High pressure of compressor
	Test when the compressor button has pressed
	Stop compressor only without affect other equipments to work. 
	Check if the input is consistent with the switch setting.

	Comp.P low
	Low pressure of compressor
	If the [LP check delay] is 0, test when the compressor button has pressed;
If the [LP check delay] is not 0, then compressor runs the test.
	
	

	Comp overload
	The compressor overload
	Compressor runs the test.
	
	Check if the input is consistent with the switch setting.

	Comp.I high
	The current of compressor is too high
	
	
	Check if the rated current of compressor1 is input is reasonable.

	Comp.I low
	The current of compressor is too low
	
	
	Check if the measure tool of the compressor1 current is connect.

	Temp.low AL
	The liquid temperature is too low
	Test after cold pump starts
	Stop the compressor and delay to stop the cool pump, and do not stop the cold pump.
	Check if the Liquid temperature is lower than the set temperature of Liquid protection.

	T.high warn
	The liquid temperature is higher than the warn value.
	
	Alarm only without affect other equipments to work.
	Check if the Liquid temperature is higher than the set temperature of Liquid warn.

	Temp.high AL
	The liquid temperature is too high
	
	Stop the compressor and delay to stop the cool pump, and do not stop the cold pump.
	Check if the Liquid temperature is higher than the set temperature of Liquid protection.

	Anti-freez.AL
	Antifreeze alarm
	Power on to test
	Stop all the compressor and cool pump, and do not stop the cold pump.
	Check if the antifreeze input is consistent with the switch setting.

	Probe break 
	The liquid temperature sensor is break
	
	
	Check if the temperature probe is in proper contact.

	Probe short
	The liquid temperature sensor is short
	
	
	

	Cool overload
	The cool pump or fan overload
	Test after Cool pump starts
	Stop compressor and cool pump or fan only
	Check if the fan1 overload input is consistent with the switch setting.

	Cool.I high
	The current of cool pump or Fan is too high
	
	
	Check if the rated current of cool is input is reasonable.

	Cool.I low
	The current of cool pump or Fan is too low 
	
	
	Check if the measure tool of the cool current is connect.

	Cool W.flow AL
	Lack of cool water flow
	Test after the cool pump starts for [Cool on delay] time
	Stop compressor and cool pump or fan only
	Check if the cool water flow input is consistent with the switch setting.

	Cold W.flow AL
	Lack of cold water flow
	Test after the cold pump starts for [Pump on delay] time
	If the [Low liquid lv] is set “Pump keep”, Stop compressor and cool pump in case of fault.

If the [Low liquid lv] is set “Pump stop”, Stop the unit in case of fault.
	Check if the cold water flow input is consistent with the switch setting.

	Pump overload
	The cold pump overload
	Test after cold pump starts
	Stop the unit 
	Check if the cold pump overload input is consistent with the switch setting.

	Pump.I high
	The current of cold pump is too high
	
	
	Check if the rated current of cold is input is reasonable.

	Pump.I low
	The current of cold pump is too low 
	
	
	Check if the measure tool of the cold current is connect.

	Phase AL
	The three-phase power input is alarm
	Power on to test
	Stop the unit
	Check if there is default phase or anti-phase in the three-phase power input and if the switch is correct.

	Water level AL
	The water level is low
	Power on to test
	If the [Lack of liquid] is set “Pump keep”, Stop compressor and cool pump in case of fault.

If the [Lack of liquid] is set “Pump stop”, Stop the unit in case of fault.
	Check if the water level input is consistent with the switch setting.

	Need Maintain
	The total time of compressor run over the allow value
	Test after cold pump starts
	The unit cannot start once stops (the accumulative operation time of compressor exceeds the set value).


12 Control

[image: image17.emf]Compressor OFF

Keep area

SV

—

SUB

SV SV+ADD

PV(℃)

Compressor ON


Control logic: 
The increase temperature process, the compressor ON when PV ≥SV + ADD.
The decrease temperature process, the compressor OFF when PV < SV – SUB

Note:  PV: The liquid temperature            SV: set temperature     

ADD: load temperature diefference     SUB: unload temperature difference

13 Manufacturer Parameters Table
Parameters set by the manufacturer and parameter meanings are listed as follows: ("*" is for parameters of the configuration wizard)

	Setting Item
	Name of Parameter
	Factory Default 
	Setting Range
	Remark

	Control Settings
	*One-Key start
	Forbid
	Forbid ~ Use
	Forbid: the compressor is allowed to ON only when 
press the compressor button;

Used: the compressor allows ON when press the pump 
button.

	
	Auto start up
	Forbid
	Forbid ~ Use
	Use: the unit starts automatically when powered on; 
Forbid: the unit doesn’t start automatically when 
powered on;

When the user parameter [On/Off type] is set to 
be"Remote", the electrical autostart is invalid.

	
	DO1 fuction
	Alarm 
signal
	Alarm signal;

Run signal
	If [DO1 fuction] is “Alarm signal”,
N.O: The 

	
	Alarm output
	Keep when mute
	Keep when 
mute;
Stop when mute
	Keep when mute: press the “alarm output” parameter to 
take 
action once a fault occurs;

Stop when mute: press the “alarm output” parameter to take action in case of no fault after silencing.

	
	Alarm type
	N.O
	N.O~N.C
	N.O: the alarm relay is ON in case of faults; 
N.C: the alarm relay is OFF in case of faults.

	
	*Low water lv.
	Pump stop
	Pump stop ~

Pump keep
	Pump stop: stop the cold pump in case of low water level fault;
Pump keep: do not stop the cold pump in case of low water level fault.

	
	*Lack of water
	Pump stop
	Pump stop ~

Pump keep
	Pump stop: stop the cold pump in case of cold water flow fault;

Pump keep: do not stop the cold pump in case of cold water flow fault.

	
	*Current detect
	Use
	Forbid ~ Use
	Use: there is a current detection module; 
Forbid: no current detection module

	
	*Comp.I rating
	0.3A
	0~35.0A
	0A: do not detect the current fault.

When [Current detect] is set “Forbid”, those parameter is not displayed.

	
	*Pump. I rating
	0.3A
	0~35.0A
	

	
	*Cool. I rating
	0.3A
	0~35.0A
	

	
	DI1 input opt
	Cool overload
	Cool overload; Anti-freezing
	Selection of switch DI1 input function 

	
	DI6 input opt
	Comp overload
	Comp overload; 
Cool W.flow
	Comp overload: DI6 input for Comp overload detection

Cool W.flow: DI9 input for cool water flow detection

	Temperature Settings
	Load offset
	1.0℃
	0~10.0℃
	Temperature deviation of load the compressor

	
	Unload offset
	1.0℃
	0~10.0℃
	Temperature deviation of unload the compressor

	
	T.setpoint max
	30.0℃
	0~99.9℃
	To limit the temperature of user set.

	
	T.setpoint min
	5.0℃
	-38.0~99.9℃
	

	
	T.bias
	0.0℃
	-9.9~9.9℃
	Compensation for the liquid temperature

	
	T.low protect
	4.0℃
	-40.0~99.9℃
	Fault of “Temp.low AL” warning is reported when the liquid temperature is lower than the set value.

	
	T.high warn
	50.0℃
	0~99.9℃
	Fault of “Temp.high warn” warning is reported when the liquid temperature is higher than the set value.

	
	T.high alarm
	60.0℃
	0~99.9℃
	Fault of “Temp.high AL” warning is reported when the liquid temperature is higher than the set value. And Stop the compressor and delay to stop the cool pump.

	
	T.high reset
	5.0℃
	0~99.9℃
	If liquid temperature<[T.high alarm]–[T.high reset], manual reset of “Temp.high AL” fault is allowed;

If liquid temperature<[T.high warn]–[T.high rese], the “Temp.high warn” fault is automatically reset;

	Time Settings
	Pump on delay
	10 S
	1~255 S
	Delay after cold pump startup.

	
	Cool on delay
	10 S
	1~255 S
	Delay after cool pump startup.

	
	Capacity ctrl.
	5 S
	0~255 S
	Control the compressor ON/OFF every [Capacity ctrl.] interval time;
For double-compressor control, if the conditions of two compressors ON are satisfied, then one of the compressors ON and the other after the time of [Capacity ctrl.].

	
	Comp protect
	60 S
	0~255 S
	To avoid frequent ON/OFF the compressor, the interval between the start of two compressors must be greater than the set value.

	
	Input stable
	2 S
	0~255 S
	The time General fault stable.

	
	W.flow stab.
	5 S
	0~255 S
	It is considered to be valid only when the water flow alarm continue for the time.

	
	LP detect dly
	60 S
	0~255 S
	Compressor low-pressure fault input is allowed only when the compressor has run for the set time.

	
	LP stable
	5 S
	0~255 S
	Low-pressure fault stable time

	
	LP stop pump
	0 S
	0~300 S
	0: the parameter has no effect .

Non-0: in case of low pressure fault of the compressor, immediately stop all compressors and cool pump, delay the [LP stop pump] and stop the cold pump.

	
	Comp operation
	0 H 
	0~9999 H
	0: this parameter has no effect.

Non-0: the compressor cannot start when the accumulative operation time is greater than the set value.

	
	Comp.I avoid
	8 S
	3~255 S
	The current fault of compressor can only be detected after compressor has started for the set time.

(When the [Current detect] is set “forbid”, the parameter is not displayed.)

	
	Pump. I avoid
	8 S
	3~255 S
	The current fault of cold pump can only be detected after it has started for the set time.

(When the [Current detect] is set “forbid”, the parameter is not displayed.)

	
	Cool. I avoid
	8 S
	3~255 S
	The current fault of cool pump can only be detected after it has started for the set time.

(When the [Current detect] is set “forbid”, the parameter is not displayed.)

	Switch Settings


	*Cool overload
	N.C
	N.O ~ N.C
	Selection of switch input mode 

N.O: switch off with no fault; 
N.C: the switch is closed with no fault.

	
	*Freez overload
	N.O
	N.O ~ N.C
	

	
	*Cold W.flow
	N.C
	N.O ~ N.C
	

	
	*W.level switch
	N.C
	N.O ~ N.C
	

	
	*Comp overload
	N.O
	N.O ~ N.C
	

	
	*Low pressure 
	N.C
	N.O ~ N.C
	

	
	*High pressure
	N.O
	N.O ~ N.C
	


[Note]: remote switch, if the remote control is used, the unit will start up when remote switch input is closed and stop when remote switch input is disconnected.
14 Electrical Connection Diagram


[image: image18.wmf]R

CPU

RY1

RY2

RY3

RY4

ICOM

AC220V

L

N

COM1

COM2

CUR1

L2

L1

CUR2

L1

S

T

FU

FU

L

N

AC220V

GW531

B

①

号

GW122B

②

号

①

号

②

号

AI1

DI3

DI4

DI5

DI6

DI7

DI8

DI1

DI2

GW122B

DO1

DO2

DO3

DO4

X1.GW531B.TY.F01M.Electrical Connection Diagram

Alarm signal/Run signal

Cool pump(Fan)

Cold pump

Compressor

N(+)

L(-)

Phase

Input

temperature

sensor

Connect GW122B

Cold

Comp

Cool

DI1:Cool overload/

Antifreezing

 switch

DI2:Remote switch

DI3:Cold Pump overload

DI4:Cold Water flow switch

DI5:Water level switch

DI6:Compressor overload/Cool Water flow switch

DI7:Low pressure of compressor

DI8:High pressure of compressor

Note:


15 Installation Dimensions


[image: image19.wmf]Machine board



[image: image20.png]_1446548623.vsd
�

℃


12.0


℃


Set


Menu


PV


Fn


Liquid temperature


Set temperature



_1446549390.vsd
�

Back


Fn


1:User setting


Enter


Function Menu


3:History List


2:Unit status


Back


Fn


Lock T.set:


Set


No


Back


Fn


T.setpoint:


Set


12.0    ℃


Enter user setting


Choice parameter


Cancel


Fn


T.setpoint:


Ok


12.0   


℃


Cancel


Fn


T.setpoint:


Ok


11.9   


℃


Back


Fn


Set


11.9    ℃


OK


OK


OK


OK


OK


OK


Enter parameter value set


Set parameter value


Save parameter value


T.setpoint:



_1446550188.vsd
�

Cancel


Enter


Config Guide


Config Guide


Enter：the screen will not    pop   up    when powered on next time



Cancel：the screen will still pop up when powered  on  next  time


℃


12.0


℃


Menu


PV


Fn


Set


Back


One-Key start:


Set


Forbid


the number  of  parameters  of configuration  wizard   and  the significance, please refer to 13 Manufacturer Parameters Table


OK


OK


Fn


Fn



_1446560672.vsd
Compressor OFF


Keep area


SV—SUB


SV


SV+ADD


PV(℃)


Compressor ON



_1446566083.dwg

_1446560209.vsd
�

Cancel


Fn


Enter


Factory debug screen


Back


Fn


Low1 press:


Alarm


Back


Fn


Pump:


ON


The result of I/O input


choice


Relay output


Manuf. Debug


Comp:


or


Relay stop output


Back


Fn


High1 Press：


Normal


Enter factory debug


OK


OK


OK


OK


Cool:


Alarm:


Pump:


Comp:


Back


Fn


OFF


Cool:


Alarm:


Pump:


Comp:


Back


Fn


ON


Cool:


Alarm:


Press



_1446551536.dwg

_1446549566.vsd
�

OK


Shift


Fn


Enter password


Ok


0***


Enter password screen


Chang password


Shift to next


Back


Fn


Enter


If password is right,
enter the factory menu 


℃


12.0


℃


Set


Menu


PV


Fn


+


4***


*0**


***1


1:Manuf.Setting


2:Manuf. Debug


3:Config Guide


OK


OK


OK


OK


Main Screen


enter password has accomplished


Enter password


Enter password


Enter password


Shift


Fn


Ok


Shift


Fn


Ok


Shift


Fn


Ok



_1446548898.vsd
Main screen


Change set temperature


Main screen



_1446549088.vsd
�

Menu


PV


Fn


Alarm


!


℃


20.5


Query


OK


℃


12.0


℃


Set


Menu


PV


Fn


Probe break


Reset


OK


Alarm screen


Current  Fault


Main screen


Back


Fn



_1446548768.vsd
�

Alarm


!


℃


20.5


Query


OK


Menu


PV


Fn


Display flickeringly


Liquid temperature


Silence&Query



_1234567896.vsd

_1234567899.vsd

_1234567902.vsd

_1446548515.vsd
Light：Remote ON/OFF is allowed
Black out：Remote ON/OFF is forbided


Black out：Comp run is not allow
Twinkle：Com run is allow
Light：Comp is running


Twinkle：Unit alarm
Black out：No alarm


To switch the comp run is Allow or not


Menu, Cancel, Back, Shift


Add value, Change page, Choose parameter


Decrease value, Change page, Choose parameter


OK, Query, Reset, Enter


Black out：Pump stoped
Twinkle：Pump stoping
Light：Pump running


Units ON/OFF



_1234567901.vsd

_1234567898.vsd

_1234567895.vsd

